## CERT OF INSP (2)
Advanced Fire & Safety, LLC
211 Jared Drive
Broussard, LA 70518
Phone: 337-330-8186 Fax: 337-330-8406
Certificate Of Inspection
Customer: | TALOS ENERGY | [6 empty] | Date: |  |  | 2017-05-10
Location: | ST-11#1 | [6 empty] | Job.#: |  |  | 17-1121
Type Of Inspection: |  |  |  | Monthly |  | Quarterly |  |  | Semi Annual |  | X | Annual |  |  | Service Call
Other
Station Bill Drawings Available? | [6 empty] | Yes |  | X | No
All Equipment Locations Been Verified As Per The Platform Station Bill? | [11 empty] | Yes |  | No
Station Bill Date: | [8 empty] | Station Bill # :
Safe Chart Date: | [8 empty] | Safe Chart #:
Comments:
------------------------------------------------------------------WORK PERFORMED ON -------------------------------------------------------------------
| Fire Fighting Equipment |  |  |  |  | Fire Detection System | [6 empty] | Safety Equipment & Warning Devices
|  | X | Hand Portable |  |  |  |  | Smoke / P.O.C | [5 empty] | X | Life Saving Equipment
|  |  | Semi Portable |  |  |  |  | Thermal
|  |  | Other |  |  |  |  | U / V | [5 empty] | X | Swing Ropes / Escape Ropes
|  |  | Other |  |  |  |  | Other
General Alarm / Paging System
| Fire Fighting System |  |  |  |  | GAS DETECTION SYSTEM | [8 empty] | Third Party USCG Inspection
|  |  | CO2 |  |  |  |  | COMB (LEL)
|  |  | Halon |  |  |  |  | TOXIC (H2s-CO-ETC.) | [6 empty] | Aids To Navigation
|  |  | DC |  |  |  |  | Oxygen
|  |  | Foam | [11 empty] | Other
|  |  | Water |  |  |  |  | Combination
|  |  | FM-200 | [11 empty] | Other
Fire Hose Reels
------------------------------------------------- INSPECTION REPORT ATTACHED FOR DETAIL -------------------------------------------------
|  | X | YES |  | NO |  |  |  |  | X | YES |  |  | No
|  | This is to certify that the equipment described herein has been inspected and/or tested as required in accordance with applicable code and mfg. recommendation. | [6 empty] | This is to certify that the equipment described herein is left in 100% proper working condition as of this certificate date.
Danny Champagne | [15 empty] | 2017-05-10
Lead Technician | [5 empty] | Customer Representative | [9 empty] | Date
Andrew Rabalais
Customer Representative (Print)

## CORRECTIONS (2)
Advanced Fire & Safety, LLC
211 Jared Drive
Broussard, LA 70518
Phone: 337-330-8186 Fax: 337-330-8406
CORRECTIONS of DEFICIENCIES
| Customer: | TALOS Energy |  | Date: |  |  | 2017-05-10
| Location | ST 11#1 |  | Job#: |  |  | 17-1121
Customer P.O.#:
No. | Location | Comments of Corrections | [5 empty] | Fixed | Initial
| NE TOP DECK | REINSTALLED SER# 572185 30# ABC AFTER IT WAS SERVICED | [5 empty] | YES | D. C.
| SW TOP DECK | REINSTALLED SER#49375 30# ABC AFTER IT WAS SERVICED | [5 empty] | YES | D. C.
| N TOP DECK | REPLACED MISSING COMPLETE RING BUOY UNIT | [5 empty] | YES | D. C.
| NW TOP DECK | REPLACED UV DAMAGED 43' ESCAPE ROPE | [5 empty] | YES | D. C.
AS per the PIC, Advanced will correct the above deficiencies. |  |  |  |  | Yes | No
As per the PIC, the customer will correct the above deficiencies. |  |  |  |  | Yes | No
2017-05-10
| Date |  | Customer Representative Signature
Andrew Rabalais
Danny Champagne
Lead Technician Signature |  |  | Customer Representative (Print)